Product Introduction
The transformer is completely hermetical oil-immersed type. The principle is the same as the hermetical power transformer. The basic elements of the amorphous alloy is Iron, nickel, cobalt, boron and carbon etc. It is a kind of isotropic soft magnetic material with low magnetizing power. With 0.027mm thickness and the filling coefficient is reduced to 0.75-0.8, the amorphous alloy material is very sensitive for stress. The electrical resistivity of the material is 3-6 times of silicon steel sheet and the hardness is 5 times of it.
Load loss of S(B)H15-M 30～1600/6～10 series transformer can be reduced by 15% on the basis of GB/T6451 standard. The no-load loss can be reduced by 70% on the base of GB/T6451 standard. Amorphous alloy transformer meets the standard JB/T10318-2002 Technical parameter of oil immersed type amorphous alloy transformer.

Model and Meaning


Technical Parameter of S(B)H15-M Series Hermetical Amorphous Alloy Power Transformer

| Rated capacity（kVA） | Voltage and tapping range |  |  | Connection Group Symbol | No-load Loss（W） | Load Loss （W）75℃ | No-load current (%) | Short-circuit impedance（%） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | High Voltage (KV) | Tapping ranges of High Voltage | Low Voltage (KV) |  |  |  |  |  |
| 30 | 6 6.3 10 10.5 11 | ±5% ±2×2.5% | 0.4 | Dyn11 ( or ) Yyn0 | 130 | 630/600 | 2.3 | 4.0 |
| 50 |  |  |  |  | 170 | 910/870 | 2.0 |  |
| 63 |  |  |  |  | 200 | 1090/1040 | 1.9 |  |
| 80 |  |  |  |  | 250 | 1310/1250 | 1.9 |  |
| 100 |  |  |  |  | 290 | 1580/1500 | 1.8 |  |
| 125 |  |  |  |  | 340 | 1890/1800 | 1.7 |  |
| 160 |  |  |  |  | 400 | 2310/2200 | 1.6 |  |
| 200 |  |  |  |  | 480 | 2730/2600 | 1.5 |  |
| 250 |  |  |  |  | 560 | 3200/3050 | 1.4 |  |
| 315 |  |  |  |  | 670 | 3830/3560 | 1.4 |  |
| 400 |  |  |  |  | 800 | 4520/4300 | 1.3 |  |
| 500 |  |  |  |  | 960 | 5410/5150 | 1.2 |  |
| 630 |  |  |  |  | 1200 | 6200 | 1.1 | 4.5 |
| 800 |  |  |  |  | 1400 | 7500 | 1.0 |  |
| 1000 |  |  |  |  | 1700 | 10300 | 1.0 |  |
| 1250 |  |  |  |  | 1950 | 12000 | 0.9 |  |
| 1600 |  |  |  |  | 2400 | 14500 | 0.8 |  |
| 2000 |  |  |  |  | 750 | 17400 | 0.20 | 5 |
| 2500 |  |  |  |  | 900 | 20200 | 0.20 |  |